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	Pos no.
	Quantity
	Unit
	Unit price
	
	Total amount
	



	1.0 
	             .........................  pc.                   ..............................  €             ..............................  €
GC Lock Control SHEV
Interface module on single or double leaf supply air door solutions, consisting of a controlled SHEV panel, retractable arm drives and motor locks for wiring and for supplying and activating the components from the SHEV panel.
Characteristics:
· Direct connection of 24 V motor locks (e.g. IQ lock EL / IQ lock EL DL)
· Connection of 12 V motor locks via a DC-to-DC converter 24 V-12 V
· Power supply in the case of a SHEV alarm via controlled SHEV panel
· Power supply in normal operation via connection of power supply units through integrated bypass boost controller
· Rectifier function when reversing polarity or resetting the SHEV panel
· Overvoltage protection at the smoke and heat extraction system input
· Integrated status display of the power supply (green LED) and the presence of a smoke and heat extraction system signal (red LED)
· Top hat rail housing with screw-fit terminals for easy wiring of the components
· Can be assembled in the GEZE surface-mounted housing or in the distribution box
Possible connections: 
· Controlled SHEV panel (24 V ± 15 %)
· K 600 T or K 600 G (direct connection of max. 2 drives)
· 12 V and/or 24 V motor locks
· Swing door drive (Powerturn F, EMD-F) / Swing door drives (Powerturn F-IS; EMD-F-IS;) 
· Push button
· or door control unit
· or access control
· and power supply units 
· A suitable power supply unit is needed to supply the motor locks during normal operation.
Technical data:
Operating voltage
                          12-24 V (-4 % +15 %)
Max. current consumption                              150 mA at 12 V / 20 mA at 24 V
Max. current drives


 4.5 A (24 V)
Max. current locks                             1.25 A at 12 V / 4.5 A at 24 V
Ambient temperature


 -5 °C...+70 °C
IP rating                                              IP20
Protection class                                              III
Max. connection cross-section
            2.5 mm²
Version:
Top hat rail housing                               grey
Dimensions W x H x D [mm]
  35 x 90 x 60 (2 HP)
Material                                                     Plastic


	1.1 
	             .........................  Pc.                   ..............................  €             ..............................  €
DC-to-DC converter
DC-to-DC converter from 24 V to 12 V for the use of 12 V motor locks in combination with the GC Lock Control SHEV on supply air door solutions.
Possible connections:
· GC Lock Control SHEV
· 12 V motor locks
Technical data: 
Operating voltage
                           9-36 V DC
Max. current consumption                               1.25 A
Max. current drives


  4.5 A (24 V)
Max. current locks                             1.25 A at 12 V / 4.5 A at 24 V
Ambient temperature


 -40 °C...+85 °C
IP rating                                                  IP20
Protection class                                                  III
Max. connection cross-section
            2.5 mm²
Version:
Top hat rail housing                               dark grey
Dimensions W x H x D [mm]
  17.5 x 90 x 54.5 
Material                                                     Plastic


	
	

	1.2 
	             .........................  pc.                   ..............................  €             ..............................  €
Power supply – NT 1.25 A – 24 V HS power supply
Power supply unit for top hat rail mounting and for supplying 24 V drives, control units and motor locks. A suitable power supply unit is needed to supply the motor locks during normal operation.
Technical data:
Output voltage                            24 V DC
Operating voltage                               230 V +/- 10%
Output current max.                          1.25 A
IP rating                                                  IP20
Version:
Top hat rail housing                               grey
Dimensions W x H x D [mm]                           72 x 93 x 56
Material                                                     Plastic


	1.3 
	             .........................  pc.                   ..............................  €             ..............................  €
Power supply – NT 2.5 A – 24 V HS power supply
Power supply unit for top hat rail mounting and for supplying 24 V drives, control units and motor locks.  A suitable power supply unit is needed to supply the motor locks during normal operation.
Technical data:
Output voltage                            24 V DC
Operating voltage                               230 V +/- 10%
Output current max.                             2.5 A
IP rating                                                  IP20
Version
Top hat rail housing                               grey
Dimensions W x H x D [mm]                           52 x 90 x 58
Material                                                     Plastic


	1.4 
	             .........................  pc.                   ..............................  €             ..............................  €
Power supply unit – Power supply unit 6.25 A - 24 V HS 
Power supply unit for top hat rail mounting and for supplying 24 V drives, control units and motor locks. A suitable power supply unit is needed to supply the motor locks during normal operation.
Technical data:
Output voltage                            24 V DC
Operating voltage                               230 V +/- 10%
Output current max.                          1.25 A
IP rating                                          IP20
 
Version
Housing                                               grey
Dimensions W x H x D [mm]                          72 x 95 x 66.5
Material                                                     Plastic
Suitable for cascading


	1.5 
	             .........................  Pc.                   ..............................  €             ..............................  €
Surface-mounted housing
Housing for surface mounting of top hat rail components such as power supply units or control units. With integrated 35 mm top hat rail for devices with a max. of 7 horizontal pitches (18 mm).
Technical data
IP rating                                             IP40
Cable routing surface-mounted or flush-mounted
 
Version
Housing                                               white
Dimensions W x H x D [mm]                          193 x 130 x 82
Material                                                     Plastic
Suitable for cascading



	1.6 
	             .........................  Pc.                   ..............................  €             ..............................  €
Installation and functional test
Installation and functional test by an expert authorised by the manufacturer.


	1.7 
	             .........................  pc.                   ..............................  €             ..............................  €
Commissioning and official approval
Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates.


	1.8 
	             .........................  pc.                   ..............................  €             ..............................  €
Service maintenance - compact package
Maintenance and testing – 2-year guarantee
Service package for maintenance and testing according to ASR A1.7 as well as according to manufacturer’s specification with the following performance features:
· One-time maintenance per contract year
· Free provision and updating of the test documents
· Attachment of the inspection sticker
· Malfunctions and repairs during the contract period are carried out at reduced hourly rates
· Service technicians are deployed within 24 hours of receipt of the notification from Monday to Friday from 7:00 - 5:00 with no surcharge
· Personal availability at the help desk 24 hours a day, 365 days a year
· Contract term: 2 years


	1.9 
	             .........................  pc.                   ..............................  €             ..............................  €
Service maintenance - comfort package
Service maintenance – 3-year guarantee
Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features:
· Extension of the warranty to 36 months
· (Requirement: the maintenance contract is concluded 3 months after the commissioning date at the latest)
· One-time maintenance per contract year
· Free provision and updating of the test documents
· Attachment of the inspection sticker
· No separate invoicing of services and travel costs during the warranty period
· No separate charge for small parts up to EUR 25 per maintenance
· No separate calculation of working time for replacement of spare parts during maintenance
· Personal availability at the help desk 24 hours a day, 365 days a year
· Contract term: 3 years


	1.10 
	             .........................  pc.                   ..............................  €             ..............................  €
Service maintenance - exclusive package
Service maintenance – warranty 5 years
Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features:
· Extension of the warranty to 60 months
· (Requirement: the maintenance contract is concluded 3 months after the commissioning date at the latest)
· One-time maintenance per contract year
· Free provision and updating of the test documents
· Attachment of the inspection sticker
· No separate invoicing of services and travel costs during the warranty period
· No separate charge for small parts up to EUR 25 per maintenance
· No separate calculation of working time for replacement of spare parts during maintenance
· Personal availability at the help desk 24 hours a day, 365 days a year
· Contract term: 5 years


	1.11 
	             .........................  pc.                   ..............................  €             ..............................  €
Delivery, assembly and commissioning
Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning by plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. 
Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in a log book.
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