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	1.0 
	             .........................  pcs.                  ..............................  €             ..............................  €
GEZE Slimdrive SL NT

Compact automatic linear sliding door with only 70 mm drive height, type-tested by the German Association for Technical Inspection according to EN 16005, for leaf weights up to 125 kg per leaf, with self-cleaning rollers for permanently smooth running
Drive
Drive dimensions H x D: 70 x 190 mm
Integrated battery with automatic charge and monitoring functions for opening or closing in the event of a power failure
Intelligent digital control (Category 2 in accordance with DIN EN 954-1 and Performance Level “d” in accordance with DIN EN ISO 13849-1):
- Convenient parameter setting, commissioning and maintenance via optional Bluetooth connection to a PC
- Self-learning and with dynamic adaptation of the passage hold-open time for optimum convenience
- Can be networked and integrated in building systems via CAN-bus
- Independent fault detection and protocol
- Adjustment options for all door movement parameters
- All functions integrated in one unit, no further modules necessary
Extremely quiet running direct current drive
Robust power supply with integrated all-pole main switch and fuse protection
Static and dynamic power limitation according to EN 16005, as well as static under 150 N in accordance with ASR A1.7 (formerly BGR 232)
Automatic reversal when obstacles are detected
Construction dimensions (dimensions in unfinished state):
Clear overall height LH:............... mm
Clear construction width LB:............... mm
Passage height DH:.............. mm
Passage clearance DB:............. mm (1-leaf 900* - 3000 mm)
*900 mm on account of DIN 18040
Type of installation:
(  ) Wall installation
or
(  ) Installation on profile system
or
(  ) Cantilever installation
Door system version:
(  ) Single-leaf closing on the left
(  ) Single-leaf closing on the right
(  ) With side parts
Fitting:
(  ) On-site moving leaf
Surface of the light alloy parts of the drive and the moving leaves if appropriate:
(  ) Anodised EV1 or (  ) RAL ........
Wiring to be carried out on site according to the GEZE cable plan by an electrical contractor.
Installation, commissioning and instruction of the operator as well as documentation handover in compliance with EN 16005 through plant fitters or service partner.
In compliance with EN 16005:
- Safety analysis must be carried out as a basis for planning and execution
- An inspection must be carried out at least 1 x year and maintenance at least 1 x year.
If there is no protection, the safety analysis must refer to the residual risk.
Activation devices:
Outside:
1 switch for opening the door (see 1.4)
1 indicator lamp (red) for visual “OCCUPIED” display, 24 V AC, white
1 emergency opening switch in a lockable box with glass pane (see 1.7)
Inside:
1 switch for opening and closing the door (see 1.4)
1 indicator lamp (red) for visual “OCCUPIED” display, 24 V AC, white


	1.1 
	             .........................  pcs.                  ..............................  €             ..............................  €
Operation

GEZE display programme switch in the AS 500 range for setting the mode of operation as well as for commissioning and setting the parameters of the drive, with control keys, 2x 7-segment display, alphanumerical fault display, IP rating IP 40
Operating modes: permanently open, automatic, shop closing, night-locking, off
( ) Surface-mounted ( ) Flush-mounted
or
GEZE keypad programme switch for setting the mode of operation, with control keys, LED dot display, coded error display, IP rating IP 40, suitable for switch product ranges with 55 x 55 mm switch unit
Operating modes: off, permanently open, automatic, shop closing, night-locking
(  ) Surface-mounted   (  ) Flush-mounted
or
GEZE mechanical programme switch for setting the mode of operation, with key, LED fault display, IP rating IP 40, suitable for switch programmes with 55 x 55 mm switch unit
Operating modes: off, permanently open, automatic, shop closing, night-locking
(  ) Surface-mounted   (  ) Flush-mounted


	1.2 
	             .........................  pcs.                  ..............................  €             ..............................  €
Operation (optional position)

GEZE key switch to “lock” the programme switch to prevent unauthorised changing of the mode of operation, IP rating IP 40
(  ) Surface-mounted   (  ) Flush-mounted
(  ) Euro profile half cylinder


	1.3 
	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)
GC 339+ active infrared detector with two light curtains for protecting the opening or closing area in accordance with EN 16005, IP54 rating, 10 possible light curtain configurations
Version:
( ) black
( ) according to RAL
( ) interior ( ) exterior
Accessories:
( ) outside: weather hood to protect the sensor from the interference of rain
( ) Ceiling installation bracket
( ) Ceiling installation kit for integrating the active infrared detector in the ceiling


	1.4 
	          .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)
GC 341 active infrared detector with two light curtains for protecting the opening or closing area according to EN 16005, IP54 rating, 4 possible light curtain configurations
Version:
( ) black
( ) interior ( ) exterior
Accessories:
(  ) outside: weather hood to protect the sensor from the interference of rain
( ) Ceiling installation bracket
( ) Ceiling installation kit for integrating the active infrared detector in the ceiling




	
	

	1.5 
	             .........................  pcs.                  ..............................  €             ..............................  €
Activation (optional position)
GEZE elbow switch, plastic, IP rating IP 30
Dimensions: 90 x 180 x 23 mm 
( ) White  ( ) Stainless steel
( ) Surface-mounted  
or
GEZE elbow switch, LS990, IP rating IP 30
Dimensions: 81 x 223 x 51 mm
( ) White  ( ) Stainless steel
( ) Surface-mounted ( ) Flush-mounted
or
GEZE elbow switch, stainless steel, IP rating IP 65
Dimensions: 72 x 250 x 17 mm 
( ) Surface-mounted
 
or
GEZE non-contact proximity switch (radar)

Plastic with antimicrobial surface, IP rating IP65, multi-colour LED feedback, adjustable acoustic feedback. Additional input to actively change the LED colour.
Dimensions: 80 x 80  mm

( ) Flush mounting 12 mm deep
( ) Surface mounting 21 mm deep
( ) Variant for WC
 
or
GEZE LED sensor push button, plastic, IP rating IP 69K
round, diameter: 100 mm
( ) Flush-mounted

( ) Surface-mounted: mounting ring flat 4 mm

( ) Surface-mounted: mounting ring high 20 mm
 
or
GEZE LED sensor push button, glass, IP rating IP 69K
round, diameter: 100 mm
( ) Flush-mounted

( ) Surface-mounted: mounting ring flat 4 mm

( ) Surface-mounted: mounting ring high 20 mm
or
GEZE LED sensor foot switch, glass, IP rating IP69K
Dimensions: 100 x 100 x 3 mm

( ) flush-mounting

( ) vertically adjustable installation base for depths of up to 215 mm from the unfinished floor

or
External lamp red, AS 500
Plastic, alpine white
IP rating IP20
Dimensions flush mounting (WxHxD) 81x81x41mm
( ) internal    ( ) external
( ) surface-mounted   ( ) flush-mounted
or
Signal horn, AS 500
Plastic, alpine white 
for acoustic signalling
Dimensions flush mounting (WxHxD) 81x81x41mm
( ) surface-mounted   ( ) flush-mounted


	1.6 
	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)

GEZE protective leaf for protecting against shearing, nipping and trapping positions according to EN 16005 in front of the moving leaf, leaves made of 10 mm ESG (toughened safety glass) including fitting, can be turned for cleaning purposes
May only be used together with fine-framed moving leaf with ISO-glass or with integrated IGG fitting.
(  ) Fastening on the drive or (  ) Fastening on the wall
alternatively:
(  ) Sensor-controlled side panel protection using 3D light curtain


	1.7 
	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)

GEZE safety leaf for protecting against shearing and nipping positions in accordance with EN 16005 with post-rail structures (depending on the offset between post surface and facade glazing) behind the moving leaf, leaf made of 10 mm ESG (toughened safety glass) incl. fitting
alternatively:
(  ) Sensor-controlled side panel protection using 3D light curtain


	1.8 
	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)
GEZE emergency stop switch with glass pane and lighting for switching off the mains voltage, IP rating IP 20
An emergency command device (emergency stop switch) is not essential for compliance with EN 16005.
(  ) Surface-mounted   (  ) Flush-mounted


	1.9 
	             .........................  pcs.                  ..............................  €             ..............................  €
Locking (optional position)
(  ) Two-stage electromagnetic locking, integrated in the drive, with manual emergency unlocking


	1.10 
	             .........................  pcs.                  ..............................  €             ..............................  €
Floor guide (optional position)

Continuous floor guide made of anodised aluminium E6/EV1, can be installed flush in the floor, guide rail can be removed for cleaning or replaced
Recommended for external doors with opening widths greater than 2000 mm


	1.11 
	             .........................  pcs.                  ..............................  €             ..............................  €
CAN interface for the connection to the building management

Technical data:
CAN interface galvanically isolated.
CAN extension module for automatic GEZE sliding door, revolving door and swing door drives as interface to connect to the GEZE building management system myGEZE Control.


	1.12 
	             .........................  pcs.                  ..............................  €             ..............................  €

Building automation connection

Building automation and control system 
For the integration of escape door control units, swing door drives, sliding doors and automatic window systems into a building management system for the use of typical building automation and control functions.
An automation controller with the following profile must be used:
BACnet device of the type BACnet Building Controller (B-BC) with tested conformity to the BACnet standard ISO 16484-5

myGEZE Control System
...... Piece basic controller as a powerful embedded PC that supports the BACnet protocol. BACnet controller of type B-BC (BACnet Building Controller / protocol audit 14)
for the integration of GEZE field bus devices. The number of fieldbus devices is specified in the specifications.

The system must be able to provide the following components (incl. software licence):

· myGEZE Control basic controller, embedded PC incl. GEZE Library 
· Terminal system for connecting the GEZE CAN bus 
· Terminal system for the connection of GEZE window technology based on 
             the IQ box KNX  
· Terminal system for connecting digital binary input signals to
             Basis of potential-free contacts 
· Terminal system for connecting digital output signals based on
potential-free door closer or changeover contacts 24 V DC     
The number of terminal systems is to be determined by the supplier on the basis of the tendered products at field level.
In top hat rail housing, incl. power supply unit, required auxiliary terminals for internal potential distribution, bus supply and bus termination.
Standard housing dimensions:  W x H x D 300 x 400 x 200 mm 
Supply voltage: 230 V AC 
incl. the following services:
· Project planning and interface configuration of the offered networking system according to GEZE standard.

· Mechanical assembly, electrical connection, commissioning
              ...........  Option                   ..............................  €             ..............................  €
Optional additional services:

Creation of project-specific wiring schematics for product systems

The service includes: 
· Creation of one basic diagram per door type
· Creation of a wiring schematic for the installed door, window and safety technology product systems
· A change index is included; additional changes charged separately
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