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	1.0 
	             .........................  pcs.                  ..............................  €             ..............................  €
GEZE swing door automatic Slimdrive EMD-F/R-IS
Double leaf with integrated closing sequence control, certified in accordance with EN 1158, for on-site fire or smoke protection doors (fire protection approval available, heed the DIBt guideline for hold-open systems) as a low-noise electromechanical swing door drive for internal and external doors, 70 mm overall height,
with hold-open mechanism in accordance with DIN 18 263 Part 4,
prepared for connection to trigger mechanism, 
with adjustable spring force EN size 4-6, 
Tested and certified in accordance with EN 16005.
Also suitable for the easy manual opening of doors (DIN 18040 optimised).
Release in the event of an alarm by integrated smoke switch under the intermediate hood of the swing door drive (the smoke switch forms a functional and visual unit with the swing door drive), with reset switch for restoring standby operation after an alarm has been triggered,
with release button (  ) flush-mounted  (  ) surface-mounted,
with mounting plate kit
Intelligent digital control (Category 2 in accordance with DIN EN 954-1 and Performance Level D in accordance with DIN EN ISO 13849-1).
Version:
(  ) for use on fire or smoke protection door
(  ) pushing, transom installation on the opposite hinge side with glide rail (EN 4-5)
(  ) pushing, transom installation on the opposite hinge side with link arm (EN 4-6)
(  ) pulling, transom installation on the hinge side with glide rail (EN 4-5)
Functions:
Operating modes: permanently open, automatic, shop closing, night
“shop closing” only in connection with an external programme switch,
Low-energy mode (low-energy drive) in accordance with EN 16005,
servo support to make the manual opening of swing doors easier,
obstruction detection and reversing,
diagnosis function and fault memory,
all settings are possible through the display programme switch
Technical features:
Dimensions: 70 x 120 mm (HxD),
Mains connection: 230 V AC, 50/60 Hz,
Door leaf width: Max. 1400 mm,
Hinge size:  
1700 – 2500 for transom installation hinge side with glide rail
1700 – 2500 for transom installation opposite hinge side with glide rail
1500 – 2800 for transom installation opposite hinge side with link arm
Door weight: Max. 230 kg
Door opening angle: approx. 110°,
Opening and closing speed adjustable,
Electrical latching action adjustable,
Hold-open time adjustable from 0 to 60 seconds,
Contour-controlled opening and closing
Connection possibilities:
Separate inputs for inner and outer sensors,
emergency-stop switch, programme switch, motor lock, on-site 
electric strike, power supply for external devices: 24 V DC, 1000 mA
Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan, commissioning to be carried out by plant fitters or service partner.
In accordance with EN 16005:
- safety analysis must be carried out as a basis for planning and execution
- after-sales service maintenance and accident prevention inspection must be carried out at least once a year
- the secondary closing edge of an automatic swing-leaf door must be secured
If there is no protection, the safety analysis must 
refer to the residual risk.
Protection of the secondary closing edge is to be carried out on site and is not part of the scope of supply of GEZE GmbH. 
We therefore recommend the use of a finger protection screen or round profiles to secure the secondary closing edge.
Note on locking:
Electric strike, for releasing the door, 24 V DC, as a counterpart to the latch lock, as well as lock switch contact to switch off the drive when the door is locked (1 piece per drive) must be provided on site.
Light alloy cover hood in the colour:
(  ) anodised EV 1
(  ) RAL .....


	1.1 
	             .........................  pcs.                  ..............................  €             ..............................  €
FT500--B
Compact electric strike for fire rated doorsets 
in fail secure version,
approved for use on fire protection doors,
for universal use right hand (ISO 5) / left hand (ISO 6)
with 3 mm adjustable radius latch,
Latch engagement depth: 6.5mm
with twin coil technology,
with bipolar EMC protective diode,
Retention force: 8000 N
Nominal voltage for momentary contact: 12-48 V AC/DC
Nominal voltage permanent operation: 12 or 24 V AC/DC
Current consumption: 100mA at 24 V
VDS Class B
Dimensions: 
15.8 x 59.5 x 25.5 mm (W x H x D)


	1.2 
	             .........................  pcs.                  ..............................  €             ..............................  €
FT501—E

Compact electric strike for fire rated doorsets 
in fail secure version, 
with signal processor and power-saving mode,
approved for use on fire protection doors,
for universal use right hand (ISO 5) / left hand (ISO 6)
with 3 mm adjustable radius latch,
Latch engagement depth: 6.5mm
with bipolar EMC protective diode,
Retention force: 8000 N
Nominal voltage for permanent operation: 8 - 24 V AC/DC
Current consumption: 200mA (at 8 – 11 V)
Current consumption: 50mA (at 12 – 24 V)
VDS Class B
Dimensions: 
15.8 x 59.5 x 25.5 mm (W x H x D)
Without strike plate


	1.3 
	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)

GEZE GC 342 laser scanner, tested in accordance with EN 16005, mounted on the door leaf, to protect the swivelling range of interior and exterior doors in the opening and closing direction. Robust enough to handle all floor conditions (e.g. entrance mat, metal rail, dark and absorbing flooring, shiny and wet tiles, grating). With integrated wall blanking and dynamic main closing edge protection.
Door leaf width: ....... mm
( ) GC 342 laser scanner kit (contains two sensors to protect both sides of the leaf)
IP rating IP54, with optimised secondary closing edge protection. If fingers are very likely to be trapped, an additional mechanical solution on the secondary closing edge can be considered. The secondary closing edge protection near the door hinges must be carried out on-site or by the door manufacturer on the basis of the safety analysis.
( ) GC 342 for hinge side and GC 342+ for the opposite hinge side
Combination of GC 342, IP rating IP54 for the hinge side and GC 342+, IP rating IP44 for the opposite hinge side. Each as an individual module (left and right variants)
 
Version:
( ) stainless steel colour
( ) black
( ) white
 
( ) Fire protection kit - master-slave replacement cable which enables cables to be guided through 5 mm instead of 10 mm bore-holes. The drilling permit must be requested from the door manufacturer.
Retrofit circuit board for connection to door cables fitted on site
( ) GC 342 Retrofit-Interface

( ) GC 342+ Retrofit-Interface

Only available for GC 342:
Protective cover to protect the laser scanner against interferences
( ) stainless steel colour
( ) black
( ) according to RAL


	1.4 
	             .........................  Stk                   ..............................  €             ..............................  €

Protection (optional position)
GEZE GC 344 solid-state scanner, tested according to EN 16005, mounted on the door leaf, for the protection of the swivelling range of internal and external doors in both opening and closing directions. Robust against all floor conditions (e.g. entrance mat, metal rail, dark and absorbent floors, shiny and wet tiles, grating) and insensitive to extraneous light or reflections. With dynamic, angle-dependent adjustment of the protection field and dynamic main closing edge protection.
Door leaf width: ....... mm
( ) GC 344 as kit (contains two sensors for the protection of both sides of the leaf) or single module
Protection class IP65, with optimised secondary closing edge protection. If there is a high risk of fingers getting caught, an additional mechanical solution at the secondary closing edge should be considered. The secondary closing edge protection in the area of the door hinges is provided on site or by the door manufacturer according to the safety analysis carried out.
 

Version:
( ) stainless steel colour
( ) black
 
Retrofit board for connection to door cables installed on site
( ) GC 342+ retrofit interface (also compatible with the GC 344)


	1.5 
	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)
GEZE safety sensors kit, in sleek narrow strip with IP rating 52, type-approved in accordance with EN 16005, installed on the door leaf, for protecting the door's swivelling range in the opening and closing direction. With integrated wall blanking (kit contains 2 safety sensors for protecting both leaf sides)
Door leaf width: ....... mm
With asymmetrical double-leaf doors with EMD-IS, EMD F-IS:
Door leaf width, active leaf: ....... mm
Door leaf width, passive leaf: ....... mm
(  ) GC 338 safety sensor kit for internal and external doors and all floor conditions (e.g. floor mat, metal rail, dark and absorbing flooring, shiny and wet tiles, grating).

Version:
( ) EV1
( ) according to RAL
(  ) GC 338 rain cover to protect the safety sensor against interference caused by rain

The secondary closing edge protection near the door hinges must be carried out on site or by the door manufacturer on the basis of the safety analysis.

GEZE linkage element with integrated sensor, for the space-saving installation of sensor and link arm or guide rail on one plane, tested in accordance with EN 16005, installed on the door leaf 
Version:

( ) GC GR, with integrated, two-part guide rail profile

( ) Adapter for the integration of the sensor strip with the link arm


	1.6 
	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)
GEZE emergency stop switch with glass pane and lighting for switching off the mains voltage, IP rating IP 20
(  ) Surface-mounted   (  ) Flush-mounted
An emergency command device (emergency stop switch) is not essential in accordance with EN 16005.


	1.7 
	             .........................  pcs.                  ..............................  €             ..............................  €

Activation (optional position)

GC 308 radar movement detector with direction detection and cross-traffic fade-out for activation, IP 54 rating, multi-colour LED feedback

Dimensions (WxHxD): 120 x 50 x 50 mm

Version:

(  ) black 

(  ) white 

(  ) stainless steel colour 

(  ) acc. to RAL

(  ) outside   (  ) inside

Accessories:

(  ) Ceiling installation kit

(  ) Ceiling bracket

(  ) exterior: weather hood


	1.8 
	             .........................  pcs.                  ..............................  €             ..............................  €

Activation (optional position)

GC 302 radar movement detector with direction detection and cross-traffic fade-out for activation, IP rating IP 54

Dimensions (WxHxD): 176 x 62 x 52 mm

Version:

(  ) black 

(  ) acc. to RAL

(  ) outside   (  ) inside

Accessories:

(  ) Ceiling installation kit

(  ) exterior: weather hood



	1.9 
	             .........................  pcs.                  ..............................  €             ..............................  €
Activation (optional position)

GEZE elbow switch, plastic, IP rating IP 30
Dimensions: 90 x 180 x 23 mm 
( ) white  ( ) stainless steel
( ) optional transmitting module 
( ) Surface-mounted  ( ) Rear panel for attaching the elbow switch to glass (in connection with the transmitting module)
or
GEZE elbow switch, LS990, IP rating IP 30
Dimensions: 81 x 223 x 51 mm
( ) white  ( ) stainless steel
( ) optional transmitting module 
( ) Surface-mounted ( ) Flush-mounted
or
GEZE elbow switch, stainless steel, IP rating IP 65
Dimensions: 72 x 250 x 17 mm 
( ) Surface-mounted
 
or
GEZE non-contact proximity switch (radar)
Plastic with antimicrobial surface, IP rating IP65, multi-colour LED feedback, adjustable acoustic feedback. Additional input to actively change the LED colour.

Dimensions: 80 x 80  mm

( ) Flush mounting 12 mm deep
( ) Surface mounting 21 mm deep
( ) Variant for WC
 
or
GEZE LED sensor push button, plastic, IP rating IP 69K
round, diameter: 100 mm
( ) Flush-mounted

( ) Surface-mounted: mounting ring flat 4 mm

( ) Surface-mounted: mounting ring high 20 mm
 
or
GEZE LED sensor push button, glass, IP rating IP 69K
round, diameter: 100 mm
( ) Flush-mounted

( ) Surface-mounted: mounting ring flat 4 mm

( ) Surface-mounted: mounting ring high 20 mm
or
GEZE LED sensor foot switch, glass, IP rating IP69K

Dimensions: 100 x 100 x 3 mm

( ) flush-mounting

( ) vertically adjustable installation base for depths of up to 215 mm from the unfinished floor



	1.10 
	             .........................  pcs.                  ..............................  €             ..............................  €
Activation (optional position)
GEZE wireless programme with secure rolling code encryption for wireless activation of the drive (approx. 30m range in the building).
Transmitter:
(  )   Wireless transmitter with 1 key, IP rating IP 54 and wall fixing
(  )   Wireless transmitter with 2 keys, IP rating IP 54 and wall fixing
(  )   Wireless transmitter with 4 keys, IP rating IP 54 and wall fixing
(  )   Transmitting module for optional integration in GEZE elbow switches
Receiver:
(  ) Receiving module with 2 outputs, 24 V, pulse mode or pulse and permanent mode for mounting in the drive or in a flush-mounted socket with enclosure rating IP 20


	1.11 
	             .........................  pcs.                  ..............................  €             ..............................  €
Activation (optional position)

GEZE GCER 300, 1-door SET
Access control solution with RFID reader and PIN keypad in stand-alone operation for controlling one door (can be extended to 2 doors). RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Two authorisation types for short-time release or continuous release (office function). Configurable door release time. Variable PIN length. Communication between reader and control unit takes place by encrypted data transfer. Functions such as interlocking door system or dementia adjustable. Release buttons can be connected.
Set comprising:
1 pc. GEZE GCER 300 I/O Box (ID no. 185707)
1 pc. GEZE GCVR 300 T, RFID reader flush-mounted (ID no. 185708)
2 pc. GEZE GCER 300 system card master (ID no. 185713)
10 pc. GEZE RFID ID card (ID no. 185711)
Optional
GEZE GCVR Touch 300 T, RFID reader flush-mounted (ID no. 187108)
GEZE RFID key fob (ID no. 185712)
GEZE GCER AP surface-mounted frame (Id. no. 130024)

or

GEZE GCER 300 Light, 1-door SET

Access control solution with RFID reader and PIN keyboard in stand-alone operation with a relay output for controlling one door located in the secured inner area. RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised for short-time release. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Configurable door release time. Variable PIN length. Communication takes place via encrypted data transfer.
Set comprising:
1 pc. GEZE GCER 300 Light, RFID reader flush-mounted (ID no. 185710)
1 pc. GEZE GCER 300 system card master (ID no. 185713)
10 pc. GEZE RFID ID card (ID no. 185711)
Optional
GEZE RFID key fob (ID no. 185712)
GEZE GCER AP surface-mounted frame (ID no. 130024)

Accessories for GCER 300 / GCER 300 Light
Plug-in power supply NT 1.0 A – 24 V DC (optional)
Primary:  230 V AC, 50 Hz
Secondary: 24 V DC (+/- 5 %) / 1 A
(ID no. 130025)

Power supply NT 1.1 A – 24 V DC flush-mounted (optional)
For installation in deep standard flush-mounted boxes
Primary:  230 V AC, 50 Hz
Secondary: 24 V DC / 1.1 A
(ID no. 151426)
Power supply NT 1.5 A – 24 V DC HA (optional)
For installation on top hat rails 
Primary: 230 V AC, 50 Hz
Secondary: 21.6 – 26.4 V DC / 1.5 A
(ID no. 151425)


	1.12 
	             .........................  pcs.                  ..............................  €             ..............................  €
Opening restrictor (optional position, an opening restrictor is necessary)
GEZE door stop to protect the door and its direct environment.


	1.13 
	             .........................  pcs.                  ..............................  €             ..............................  €
Opening restrictor (optional position, an opening restrictor is necessary)
GEZE integrated opening restrictor, can be retrofitted to the glide rail on site.
Area of application: internal doors


	1.14 
	             .........................  pcs.                  ..............................  €             ..............................  €
Operation (optional position)
GEZE display programme switch in the AS 500 range for setting the mode of operation as well as for commissioning and parameterisation of the drive, with function keys, 2x 7-segment display, alphanumerical fault display, IP rating IP 40
Operating modes: permanently open, automatic, shop closing, night-locking
 (  ) Surface-mounted   (  ) Flush-mounted
or
GEZE key programme switch for setting the operating mode, with control keys, LED dot display, coded error display, IP rating IP 40, suitable for switch product ranges with 55 x 55 mm switch insert
Operating modes: off, permanently open, automatic, shop closing-time, night-locking
(  ) Surface-mounted   (  ) Flush-mounted
or
GEZE mechanical programme switch for setting the operating mode, with rotary button, LED fault display, IP rating IP 40, suitable for switch programmes with 55 x 55 mm switch insert
Operating modes: off, permanently open, automatic, shop closing-time, night-locking
(  ) Surface-mounted   (  ) Flush-mounted
or
GEZE mechanical programme switch for setting the operating mode, with key, LED fault display, IP rating IP 40, suitable for switch programmes with 55 x 55 mm switch insert
Operating modes: off, permanently open, automatic, shop closing-time, night-locking
(  ) Surface-mounted   (  ) Flush-mounted


	1.15 
	             .........................  pcs.                  ..............................  €             ..............................  €
Operation (optional position)
GEZE key switch to “lock” the programme switch to prevent unauthorised changing of the operating mode, IP rating IP 40
(  ) Surface-mounted   (  ) Flush-mounted


	1.16 
	             .........................  pcs.                  ..............................  €             ..............................  €

CAN interface for the connection to the building management

Technical data:
CAN interface galvanically isolated.
CAN extension module for automatic GEZE sliding door, revolving door and swing door drives as interface to connect to the GEZE building management system myGEZE Control.


	1.17 
	             .........................  pcs.                  ..............................  €             ..............................  €

Building automation connection

Building automation and control system 
For the integration of escape door control units, swing door drives, sliding doors and automatic window systems into a building management system for the use of typical building automation and control functions.
An automation controller with the following profile must be used:
BACnet device of the type BACnet Building Controller (B-BC) with tested conformity to the BACnet standard ISO 16484-5

myGEZE Control System
...... Piece basic controller as a powerful embedded PC that supports the BACnet protocol. BACnet controller of type B-BC (BACnet Building Controller / protocol audit 14)
for the integration of GEZE field bus devices. The number of fieldbus devices is specified in the specifications.

The system must be able to provide the following components (incl. software licence):

· myGEZE Control basic controller, embedded PC incl. GEZE Library 
· Terminal system for connecting the GEZE CAN bus 
· Terminal system for the connection of GEZE window technology based on 
             the IQ box KNX  
· Terminal system for connecting digital binary input signals to
             Basis of potential-free contacts 
· Terminal system for connecting digital output signals based on
potential-free door closer or changeover contacts 24 V DC     
The number of terminal systems is to be determined by the supplier on the basis of the tendered products at field level.
In top hat rail housing, incl. power supply unit, required auxiliary terminals for internal potential distribution, bus supply and bus termination.
Standard housing dimensions:  W x H x D 300 x 400 x 200 mm 
Supply voltage: 230 V AC 
incl. the following services:
· Project planning and interface configuration of the offered networking system according to GEZE standard.

· Mechanical assembly, electrical connection, commissioning
              ...........  Option                   ..............................  €             ..............................  €
Optional additional services:

Creation of project-specific wiring schematics for product systems
The service includes: 
· Creation of one basic diagram per door type
· Creation of a wiring schematic for the installed door, window and safety technology product systems
· A change index is included; additional changes charged separately


	1.18 
	             .........................  pcs.                  ..............................  €             ..............................  €
Acceptance test (optional position)
Acceptance test for the hold-open system and permanent attachment of the sign of approval
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