Tender text myGEZE Control building automation and control system Version 0.1
Status: 24.07.25
	Project:
	

	Support:
	

	Spec. no:
	
	Site:
	


	Pos no.
	Quantity
	Unit
	Unit price
	
	Total amount
	



	1.0 
	             .........................  pcs.                  ..............................  €             ..............................  €
Building automation and control system 
For the integration of escape door control units, swing door drives, sliding doors and automatic window systems into a building management system for the use of typical building automation and control functions.
An automation controller with the following profile must be used:
· BACnet device of the type BACnet Building Controller (B-BC) with tested conformity to the BACnet standard ISO 16484-5

	


	
	             .........................  pcs.                  ..............................  €             ..............................  €
myGEZE Control System
...... Piece basic controller as a powerful embedded PC that supports the BACnet protocol. BACnet controller of type B-BC (BACnet Building Controller / protocol audit 14)
for the integration of GEZE field bus devices. The number of fieldbus devices is specified in the specifications.
The system must be able to provide the following components (incl. software licence):
· myGEZE Control basic controller, embedded PC incl. GEZE Library 
· Terminal system for connecting the GEZE CAN bus 
· Terminal system for the connection of GEZE window technology based on 
             the IQ box KNX  
· Terminal system for connecting digital binary input signals to
             Basis of potential-free contacts 
· Terminal system for connecting digital output signals based on
potential-free door closer or changeover contacts 24 V DC     
The number of terminal systems is to be determined by the supplier on the basis of the tendered products at field level.
In top hat rail housing, incl. power supply unit, required auxiliary terminals for internal potential distribution, bus supply and bus termination.
Standard housing dimensions:  WxHxD 300 x 400 x 200 mm 
Supply voltage: 230 V AC 
incl. the following services:
· Project planning and interface configuration of the offered networking system according to GEZE standard.
· Mechanical assembly, electrical connection, commissioning


	1.1 
	......................... Option                   ..............................  €             ..............................  €
Optional additional services:



Creation of project-specific wiring schematics for product systems
· The service includes:

· Creation of a wiring schematic for each system type

· Creation of a networking plan for the installed product systems door, window and safety technology

· A change index is included

· Wiring diagrams can be ordered as an additional service
Participation in an additional appointment
A planning and coordination meeting / Construction meeting with the client and other trades in the planning phase
........  pcs. 
as online appointment
........  pcs. 
as appointment on site, incl. journey
Project monitoring/coordination

Project planning activities necessary to coordinate the smooth running of a project. Project planning activities include, for example, preliminary testing of the doors.
........  pcs. 
Appointment on site, incl. journey
Hourly labour and additional trip to site
Hourly charges for additional work and services. Billing based on time and work performed, with documentation.
...................1 hour  Option                   .......................  €             ..............................  €
...................1 approach  Option                   ................  €             ..............................  €
	1.2 
	............................  Option                   .......................... €             ..............................  €
Accessories
CAN interface door system
 
CAN extension module galvanically isolated for automatic sliding door, revolving door and swing door drives as an interface for connection to the GEZE building management system myGEZE Control.
Assembly, electrical connection and CAN addressing



	1.3 
	............................  Option                   ..............................  €             ..............................  €

Accessories
CAN-Interface SHEV panel
 
CAN extension module galvanically isolated for smoke and heat extraction control units (MBZ) for connection to the GEZE building management system myGEZE Control.
Assembly, electrical connection and CAN addressing
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