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_________________________________________________________________________________
Pos. no.

Quantity

Unit   
Unit price

Total amount
_________________________________________________________________________________

	1.0 
	              .........                   pcs.                     .................. €                   .................. €
GEZE MBZ 300 N8
Modular bus control panel for smoke and heat extraction and ventilation. For controlling 24 V DC electric drives with an overall power consumption of 8 ampere.
Commissioning with default settings without further parameter setting makes fast and straightforward installation possible.
USB interface for the comprehensive parameter setting using MBZ 300 PC configuration software.  
The control panel has free slots for a further module and can be extended by:
- vent group (Drive Module DM)
- status contacts (relay module ERM)
- weather sensors (weather module WM)   
Automatic battery charger for temperature-compensated charging with monitoring of the charging equipment
Automatic switchover from mains to battery operation
Emergency power supply with rechargeable battery 2 x 12 V for at least 72 hours
Possible connections:
- Rain/wind control
- Smoke detector and/or heat detector
- FT 4 SHEV button 
- Vent switch with or without LED function display
- Alarm input for external release (fire alarm system)
Technical data:
Input voltage: 230 V AC
Output voltage: 24 V DC
Residual ripple: 2 %
Integrated service interval display
IP rating: IP54
Output current max. 8 A
Tested in accordance with EN12010-10 and VdS approved
Steel cabinet with two-way key bit lock, painted grey (RAL 7035)
Width: 300 mm
Height:  400 mm
Depth:  200 mm
One alarm group with:
Connection of automatic detectors and line monitoring in
- max. two separately evaluated lines
- max. 10 each
Connection option for a line-monitored external potential-free contact e.g. fire alarm system
Connection of SHEV buttons with line monitoring
Inputs for central vent switch
Parameters for push button properties can be set for
- Dead man or latching
- Automatic step
- Automatic ventilation
Potential-free status contact for alarm or fault, parameters can be set
Status display for the module and connected components via LEDs for high operating comfort during installation and servicing.
One vent group with:
8 A switching current
Status inputs for which parameters can be set
- as inhibiting input for sequence control with shades
- as input for feedback of the end positions OPEN and CLOSED
Parameters for push button properties can be set for
- Dead man or latching
- Automatic step
- Automatic ventilation
Motor connection with line monitoring
Supply to holding magnets possible
Activation of pressure gas generators
Short-circuit proof due to automotive flat fuse
Direct activation of the module via operating buttons on the module for convenient start-up
Status display for the module and connected components via LEDs for high operating comfort during installation and servicing.


	1.1 
	              .........                   pcs.                     .................. €                   .................. €
GEZE MBZ 300 DM drive module 
For use in the GEZE MBZ 300 modular bus emergency power control panel
For controlling 24 V DC electric drives with max. 8 ampere switching current.


	1.2 
	              .........                   pcs.                     .................. €                   .................. €
GEZE MBZ 300 series terminal set
For use in the GEZE MBZ 300 modular bus emergency power control panel
For the connection of drives with larger cable diameter e.g. to the DME


	1.3 
	              .........                   pcs.                     .................. €                   .................. €
GEZE MBZ 300 SM sensor module 
For use in the GEZE MBZ 300 modular bus emergency power control panel
For evaluating line-monitored alarm lines, formation of fire sections and ventilation control


	1.4 
	              .........                   pcs.                     .................. €                   .................. €
GEZE MBZ 300 WM weather module 
For use in the GEZE MBZ 300 emergency power control panel
For the evaluation of weather sensors and / or for the activation of smoke and heat extraction windows (SHEV) depending on the wind direction.
Lockable components for different requirements:
· GEZE rain/wind control with potential-free contacts for ventilation
· GC 401 RS rain sensor and GC 402 WVS wind sensor with adjustment of the max. wind speed for ventilation via the MBZ 300 software
· GC 401 RS  rain sensor and GC 402 WVS wind sensor and GC 403 WDS wind direction sensor as complete activation for SHEVs depending on the wind direction in accordance with EN 12101 Part 2
The settings are made using the MBZ 300 software.
Status display for the module and connected components via LEDs for high operating comfort during installation and servicing.


	1.5 
	              .........                   pcs.                     .................. €                   .................. €
GEZE MBZ 300 ERM relay module 
For use in the GEZE MBZ 300 emergency power control panel
6 potential-free status contacts for which parameters can be set for forwarding alarm, fault or ventilation signals
The settings are made using the MBZ 300 software.
Status display for the module and connected components via LEDs for high operating comfort during installation and servicing.


	1.6 
	              .........                   pcs.                     .................. €                   .................. €
GEZE MBZ 300 CAN module

For networking several MBZ 300:

Interface module for connection to building management systems with myGEZE Control

Every linked control panel needs a CAN module. Settings per MBZ 300 Software.
Possibilities:

· superior alarm groups

· superior ventilation groups

· superior weather groups



	1.7 
	              .........                   pcs.                     .................. €                   .................. €
GEZE IO 420 interface module
Module for connecting MBZ 300 via input and output terminals or CAN Bus to BACnet MS/TP. 
Makes activation of the vent groups via GEZE Cockpit possible. Makes visualisation of MBZ 300 alarm and fault messages possible on GEZE Cockpit.


	1.8 
	              .........                   pcs.                     .................. €                   .................. €
GEZE FT 4 K/24 V DC SHEV button
for manual alarm triggering with
alarm and reset button and LED display for "Fire alarm", "Operation", "Window
open" and "Fault", in lockable surface-mounted housing marked "Smoke extraction", with break glass pane, plastic housing in the colour:
orange similar to RAL 2011


	1.9 
	              .........                   pcs.                     .................. €                   .................. €
GEZE FT4 A/24 V DC SHEV button – VdS

for manual alarm triggering with alarm and reset button and LED display for "Fire alarm", "Operation", "Window open" and "Fault", in lockable surface-mounted housing marked "Smoke vent", with break glass pane, die-cast housing in the colour

Colour:

orange RAL 2011 (VdS approval)
Alternatively:
(  ) red RAL 3000
(  ) blue RAL 5015
(  ) yellow RAL 1021
(  ) grey RAL 7035

(  ) secondary unit, orange RAL 2011 (only with LED alarm)
(  ) acoustic, orange RAL 2011 (with signal in the case of alarm, fault)



	1.10 
	              .........                   pcs.                     .................. €                   .................. €
GEZE RM 1003/24 V DC smoke detector with base,
for automatic alarm triggering in the case of smoke,
VdS-approved version (G 205091)


	1.11 
	              .........                   pcs.                     .................. €                   .................. €
GEZE WM 1005/24 V DC heat detector with base for automatic alarm triggering in the case of heat development,
VdS-approved version (G 205092)


	1.12 
	              .........                   pcs.                     .................. €                   .................. €
GEZE GC 162 RWA smoke detector with base
Ceiling-mounted detector for automatically triggering an alarm in the case of smoke,
simple testing using an integrated magnetic sensor, 
Tested in accordance with EN 54-7


	1.13 
	              .........                   pcs.                     .................. €                   .................. €
GEZE GC 163 RWA heat detector with base
Ceiling-mounted detector for automatically triggering an alarm in the case of heat build-up,
simple testing using an integrated magnetic sensor, 
Tested in accordance with EN 54-5


	1.14 
	              .........                   pcs.                     .................. €                   .................. €
GEZE vent switch for ventilation mode
(  ) AS 500 vent switch LTA-24-AZ with control keys “Open-Close” and LED function display, IP rating IP40, to match switch ranges with 55 x 55 mm switch insert,
(  ) Surface-mounted
(  ) Flush-mounted


	1.15 
	              .........                   pcs.                     .................. €                   .................. €
GEZE E 70 room temperature regulator
for automatic control of the room temperature
Adjustment of room temperature from 5 °C to 30 °C and
switchover manual-automatic operation,
(1 piece)


	1.16 
	              .........                   pcs.                     .................. €                   .................. €
GEZE GC 240 RS rain sensor 
for the automatic closing of windows in case of rain in ventilation mode, rain sensor (heated electrically) with integrated control panel (1 piece)


	1.17 
	              .........                   pcs.                     .................. €                   .................. €
GEZE rain/wind control
for the automatic closing of windows in case of rain/wind in ventilation mode, consisting of weather station with rain and wind sensor (heated electrically), control panel (1 piece)


	1.18 
	REMARK

Electrical cable routing and connection on site by an electrical contractor according to the GEZE cable diagrams. The type of cable to be used is to be determined with the respective local authorities.



	1.19 
	              .........                   pcs.                     .................. €                   .................. €
GEZE weather sensor system
comprising
(  ) GC 401 RS rain sensor
(  ) GC 402 WVS wind sensor
(  ) GC 403 WDS wind direction sensor (rain and wind sensor needed)
For the automatic rain/wind control of ventilation operation and / or activation of SHEV depending on the wind direction (setting via the MBZ 300 software)


	1.20 
	             .........................  pcs.                  ..............................  €             ..............................  €

Building automation connection

Building automation and control system 
For the integration of escape door control units, swing door drives, sliding doors and automatic window systems into a building management system for the use of typical building automation and control functions.
An automation controller with the following profile must be used:
BACnet device of the type BACnet Building Controller (B-BC) with tested conformity to the BACnet standard ISO 16484-5

myGEZE Control System
...... Piece basic controller as a powerful embedded PC that supports the BACnet protocol. BACnet controller of type B-BC (BACnet Building Controller / protocol audit 14)
for the integration of GEZE field bus devices. The number of fieldbus devices is specified in the specifications.

The system must be able to provide the following components (incl. software licence):

· myGEZE Control basic controller, embedded PC incl. GEZE Library 
· Terminal system for connecting the GEZE CAN bus 
· Terminal system for the connection of GEZE window technology based on 
             the IQ box KNX  
· Terminal system for connecting digital binary input signals to
             Basis of potential-free contacts 
· Terminal system for connecting digital output signals based on
potential-free door closer or changeover contacts 24 V DC     
The number of terminal systems is to be determined by the supplier on the basis of the tendered products at field level.
In top hat rail housing, incl. power supply unit, required auxiliary terminals for internal potential distribution, bus supply and bus termination.
Standard housing dimensions:  W x H x D 300 x 400 x 200 mm 
Supply voltage: 230 V AC 
incl. the following services:
· Project planning and interface configuration of the offered networking system according to GEZE standard.

· Mechanical assembly, electrical connection, commissioning

              ...........  Option                   ..............................  €             ..............................  €

Optional additional services:

Creation of project-specific wiring schematics for product systems

The service includes: 
· Creation of one basic diagram per door type
· Creation of a wiring schematic for the installed door, window and safety technology product systems
· A change index is included; additional changes charged separately


	1.20
	              .........                   pcs.                     .................. €                   .................. €
Installation and functional test
Installation and functional test by an expert authorised by the manufacturer.


	1.21
	              .........                   pcs.                     .................. €                   .................. €
Start-up and official approval
Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates.


	1.22
	              .........                   pcs.                     .................. €                   .................. €
Maintenance and testing of smoke and heat extraction systems

(optional position)

Service package for maintenance and testing according to ASR A1.6, DIN 18232 as well as according to manufacturer’s specification with the following performance features:

- One maintenance per contract year

- Free provision and updating of the test documents

- Attachment of the inspection sticker

- Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates

- Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges

- Personal availability at the help desk 24 hours a day, 365 days a year

- Contract run time: 2 years



	1.23
	Service maintenance - comfort package

Service maintenance (optional position)

Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.6, DIN 18232 as well as according to manufacturer’s specification with the following performance features:

- Extension of the warranty to 36 months

(condition: the maintenance contract is concluded 3 months after the commissioning date at the latest)

- One maintenance per contract year

- Free provision and updating of the test documents

- Attachment of the inspection sticker

- No separate charging for services and travel costs during the warranty period

- No separate charging for consumables up to € 25 per maintenance

- No separate charging for working hours when spare parts are replaced during the maintenance

- Personal availability at the help desk 24 hours a day, 365 days a year

- Contract run time: 3 years



	1.24
	              .........                   pcs.                     .................. €                   .................. €
Delivery and installation
Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. 
Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log.
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