Tender Text Slimdrive SL-FR-RC2                                           Version 2.4
Status: 24.03.26
	Project:
	

	Support:
	

	Spec. no.:
	
	Site:
	


	Pos no.
	Quantity
	Unit
	Unit price
	
	Total amount
	



	1.0 
	             .........................  pcs.                   ..............................  €             ..............................  €

GEZE Slimdrive SL-FR-RC2
Modular compact automatic linear sliding door with only 70 mm drive height for use in emergency exit routes, RC2-tested in accordance with DIN EN 1627 to 1630, TÜV type-tested in accordance with EN 16005, with 2-motor technology, for leaf weights up to 120 kg per leaf.

Redundant emergency exit function through 2-motor technology, with duplicate processing system and low wear

Monitored battery for emergency opening in the event of a power failure

Redundant digital control (Category 2 in accordance with DIN EN 954-1 and Performance Level D  in accordance with DIN EN ISO 13849-1):
- Self-learning

- Optimum convenience thanks to automatic adaptation of door behaviour to through-traffic

- Can be linked and integrated in building systems via CAN-bus

- Independent fault detection and protocol

- Setting possibilities for all door movement parameters

- All functions integrated in one unit, no further modules necessary

Extremely smooth-running DC drive

Sturdy power supply with integrated all-pole main switch and fuse protection

Static and dynamic power limitation in accordance with EN 16005, as well as static under 150 N in accordance with ASR A1.7 (formerly BGR 232)
Automatic reversal when obstacles are detected

Drive functions (H x D): 70 x 189 mm

- Reinforced roller carriage version

- Additional mechanical protection in the upper horizontal area
(  ) Mounting sub-structure for supporting angle for stable fixing on unfinished floor

Locking:
Bi-stable electromechanical rod locking, invisibly integrated in the profile system, with manual emergency unlocking in the drive

(  ) Mounting sub-structure for floor plate for the rod locking mechanism for stable fixing on unfinished floor

Additional variants for more safety and convenience:

(  ) FR-RWS

For use in escape route systems with locked emergency exit route and emergency opening switch, with TÜV report for acceptance in individual cases (has to be applied for by the client) *

(  ) FR-LL

For locked one-way or shop closed function, TÜV type-tested

(  ) FR-DUO

With emergency exit function in both directions, TÜV type-tested

*The use of an emergency push-button is compulsory for the RWS operating mode, with all other variants an emergency command device (emergency switch) does not have to be used.

Type of installation:

(  ) Wall mounting

or

(  ) Mounting on profile system

Construction dimensions (dimensions in unfinished state):

Clear overall height LH:............... mm

Clear overall width LW:............... mm

Passage height PH:.............. mm (max. 3000 mm)

Passage clearance PC:............. mm (double-leaf 900 - 3000 mm)

Area of application:

Number of leaves
(  ) single leaf, right hand slide to open

(  ) single leaf, left hand slide to open

(  ) double-leaf

(  ) with side parts

Fitting:

(  ) moving leaf with ISO or mono-safety glass fine-framed (up to 120 kg leaf weight):

     (  ) with ISO (safety glass P4A) <23.5 mm sealed on the internal and external moving leaf edge

     (  ) with laminated safety glass (P4A) <23.5 mm sealed on the internal and external moving leaf edge

Surface of the light alloy parts of the drive and the moving leaves if appropriate:

(  ) anodised EV1

or

(  ) RAL ........

Wiring to be carried out on site according to the GEZE cable diagram by an electrical contractor.

Installation, start-up and instruction of the operator as well as documentation handover in accordance with EN 16005 through plant fitters or service partner.

In accordance with EN 16005:

- safety analysis must be carried out as a basis for planning and execution

- an inspection must be carried out at least 1 x year and maintenance at least 2 x year

Note:
The burglar-resistant function RC2 is only enabled in "NIGHT" mode. In "NIGHT" mode the door does not fulfil any emergency exit requirements. It is necessary to ensure that there is nobody in the building or that sufficient other emergency exits are available.
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	             .........................  pcs.                   ..............................  €             ..............................  €

Floor guide

(  ) Selective floor guide, made of anodised E6/EV1 aluminium, can be mounted on finished floor level

(  ) Mounting base for supporting bracket for stable mounting to unfinished floor

or

(  ) Continuous floor guide, made of aluminium, anodised E6 C-0 (EV1), can be mounted flush with the floor, guide rail can be removed or replaced for cleaning, including mounting base for supporting bracket for stable mounting to unfinished floor

Recommended for external doors with opening widths greater than 2000 mm
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	             .........................  pcs.                   ..............................  €             ..............................  €

Operation

GEZE display programme switch for setting the mode of operation as well as for putting the drive into operation and setting parameters, with function keys, 2 x 7-segment display, alpha-numerical fault display, enclosure rating IP 40

Modes of operation: permanently open, automatic, shop closing, night-locking

(  ) Surface-mounted   (  ) Flush-mounted
or

GEZE key programme switch for setting the operating mode, with function keys, LED matrix display, coded fault display, enclosure rating IP 40, suitable for switch programmes with 55 x 55 mm switch insert

Modes of operation: off, permanently open, automatic, shop closing, night-locking

(  ) Surface-mounted   (  ) Flush-mounted
or

GEZE mechanical programme switch for setting the operating mode, with key, LED fault display, enclosure rating IP 40, suitable for switch programmes with 55 x 55 mm switch insert

Modes of operation: off, permanently open, automatic, shop closing, night-locking

(  ) Surface-mounted   (  ) Flush-mounted

According to AutSchR and EN 16005 the programme switch must be secured against unauthorised adjustment on FR doors:
GEZE key switch to “lock” the programme switch to prevent unauthorised changing of the operating mode, IP rating IP 40
(  ) Surface-mounted   (  ) Flush-mounted
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Activation and protection (optional position)
GC 363+ combined detector with direction detecting radar movement detector for activation and active infrared detector with two light curtains for protection of the opening or closing area in accordance with EN 16005, IP54 rating, 10 possible light curtain configurations
Version:
( ) black
( ) according to RAL
(  ) outside   (  ) inside
Accessories:
(  ) outside: weather hood to protect the sensor from the interference of rain
(  ) Ceiling installation bracket
(  ) Ceiling installation kit for integrating the sensor in the ceiling
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	             .........................  pcs.                  ..............................  €             ..............................  €
Activation and protection (optional position)
GC 365 combined detector with direction detecting radar movement detector for activation and active infrared detector with two light curtains for protection of the opening or closing area in accordance with EN 16005, IP54 rating, 4 possible light curtain configurations
Version:
( ) black
( ) outside   ( ) inside
Accessories:
( ) outside: weather hood to protect the sensor from the interference of rain
( ) Ceiling installation bracket
( ) Ceiling installation kit for integrating the sensor in the ceiling
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	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)
GC 339+ active infrared detector with two light curtains for protecting the opening or closing area in accordance with EN 16005, IP54 rating, 10 possible light curtain configurations
Version:
( ) black
( ) according to RAL
( ) interior ( ) exterior
Accessories:
( ) outside: weather hood to protect the sensor from the interference of rain
( ) Ceiling installation bracket
( ) Ceiling installation kit for integrating the active infrared detector in the ceiling
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Activation (optional position)

GEZE elbow switch, plastic, IP rating IP 30
Dimensions: 90 x 180 x 23 mm 
( ) white  ( ) stainless steel
( ) optional transmitting module 
( ) Surface-mounted  ( ) Rear panel for attaching the elbow switch to glass (in connection with the transmitting module)
or
GEZE elbow switch, LS990, IP rating IP 30
Dimensions: 81 x 223 x 51 mm
( ) white  ( ) stainless steel
( ) optional transmitting module 
( ) Surface-mounted ( ) Flush-mounted
or
GEZE elbow switch, stainless steel, IP rating IP 65
Dimensions: 72 x 250 x 17 mm 
( ) Surface-mounted
 
or
GEZE non-contact proximity switch (radar)
Plastic with antimicrobial surface, IP rating IP65, multi-colour LED feedback, adjustable acoustic feedback. Additional input to actively change the LED colour.

Dimensions: 80 x 80  mm

( ) Flush mounting 12 mm deep
( ) Surface mounting 21 mm deep
( ) Variant for WC
 
or
GEZE LED sensor push button, plastic, IP rating IP 69K
round, diameter: 100 mm
( ) Flush-mounted

( ) Surface-mounted: mounting ring flat 4 mm

( ) Surface-mounted: mounting ring high 20 mm
 
or
GEZE LED sensor push button, glass, IP rating IP 69K
round, diameter: 100 mm
( ) Flush-mounted

( ) Surface-mounted: mounting ring flat 4 mm

( ) Surface-mounted: mounting ring high 20 mm
or
GEZE LED sensor foot switch, glass, IP rating IP69K

Dimensions: 100 x 100 x 3 mm

( ) flush-mounting

( ) vertically adjustable installation base for depths of up to 215 mm from the unfinished floor
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Activation (optional position)

GEZE wireless programme with secure rolling code encryption for wireless drive activation (range of approx. 30 m in the building).

Transmitter:

(  )   Wireless transmitter with 1 key, enclosure rating IP 54 and wall fixing

(  )   Wireless transmitter with 2 keys, enclosure rating IP 54 and wall fixing

(  )   Wireless transmitter with 4 keys, enclosure rating IP 54 and wall fixing

(  )   Wireless transmitter module for optional integration in the GEZE elbow switch
Radio receiver:

(  )   Radio receiver module with 2 outputs, 24 V, pulse mode or pulse and

       permanent mode for mounting in the drive or in a flush-mounted socket with enclosure rating IP 20
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Activation (optional position)

GEZE GCER 300, 1-door SET
Access control solution with RFID reader and PIN keypad in stand-alone operation for controlling one door (can be extended to 2 doors). RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Two authorisation types for short-time release or continuous release (office function). Configurable door release time. Variable PIN length. Communication between reader and control unit takes place by encrypted data transfer. Functions such as interlocking door system or dementia adjustable. Release buttons can be connected.
Set comprising:
1 pc. GEZE GCER 300 I/O Box (ID no. 185707)
1 pc. GEZE GCVR 300 T, RFID reader flush-mounted (ID no. 185708)
2 pc. GEZE GCER 300 system card master (ID no. 185713)
10 pc. GEZE RFID ID card (ID no. 185711)
Optional
GEZE GCVR Touch 300 T, RFID reader flush-mounted (ID no. 187108)
GEZE RFID key fob (ID no. 185712)
GEZE GCER AP surface-mounted frame (Id. no. 130024)

or
GEZE GCER 300 Light, 1-door SET

Access control solution with RFID reader and PIN keyboard in stand-alone operation with a relay output for controlling one door located in the secured inner area. RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised for short-time release. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Configurable door release time. Variable PIN length. Communication takes place via encrypted data transfer.
Set comprising:
1 pc. GEZE GCER 300 Light, RFID reader flush-mounted (ID no. 185710)
1 pc. GEZE GCER 300 system card master (ID no. 185713)
10 pc. GEZE RFID ID card (ID no. 185711)
Optional
GEZE RFID key fob (ID no. 185712)
GEZE GCER AP surface-mounted frame (ID no. 130024)

Accessories for GCER 300 / GCER 300 Light
Plug-in power supply NT 1.0 A – 24 V DC (optional)
Primary:  230 V AC, 50 Hz
Secondary: 24 V DC (+/- 5 %) / 1 A
(ID no. 130025)

Power supply NT 1.1 A – 24 V DC flush-mounted (optional)
For installation in deep standard flush-mounted boxes
Primary:  230 V AC, 50 Hz
Secondary: 24 V DC / 1.1 A
(ID no. 151426)
Power supply NT 1.5 A – 24 V DC HA (optional)
For installation on top hat rails 
Primary: 230 V AC, 50 Hz
Secondary: 21.6 – 26.4 V DC / 1.5 A
(ID no. 151425)
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Activation (optional position)

GEZE key switch outside (enclosure rating IP 54) with or without profile half cylinder and switch function 
(  ) Surface-mounted   (  ) Flush-mounted
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	             .........................  pcs.                   ..............................  €             ..............................  €

Activation (optional position)

GEZE key switch outside (enclosure rating IP 54) with or without profile half cylinder and catch function for the fire brigade
(  ) Flush-mounted
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Activation (optional position)

GEZE key switch outside (enclosure rating IP 54), prepared for on-site profile half cylinder from the locking system as well as 1 push button with key symbol for opening from the inside. On contact, the system opens from its locked position once outwards and inwards, and locks again after the leaf has reached the closed position.
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Activation (optional position)

GEZE auxiliary button for limited opening width
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Protection (optional position)
GEZE protective leaf for protecting against shearing, nipping and trapping positions in accordance with EN 16005 in front of the moving leaf, leaves made of 10 mm toughened safety glass  including door fitting, can be turned for cleaning purposes
May only be used together with fine-framed moving leaf with ISO-glass.
(  ) fastening on the drive or (  ) fastening on the wall
alternatively:
(  ) sensor-controlled fixed panel protection using 3D light curtain
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Protection (optional position)
GEZE safety leaf for protecting against shearing and nipping spots in accordance with EN 16005 with post-rail structures (depending on the distance between post surface and facade glassing) behind the moving leaf, leaf made of 10 mm toughened safety glass  incl. fitting

alternatively:

(  ) sensor-controlled fixed panel protection using 3D light curtain
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Protection (optional position)

GEZE emergency stop switch with glass pane and light, for switching off the mains voltage, enclosure rating IP 20

An emergency command device (emergency stop switch) is not essential in accordance with EN 16005.

(  ) Surface-mounted   (  ) Flush-mounted
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Protection (optional position)

GEZE emergency stop switch with illuminated mushroom button for emergency opening or unlocking, enclosure rating IP 40

An emergency command device (emergency stop switch) is not essential in accordance with EN 16005.

(  ) Surface-mounted   (  ) Flush-mounted
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	             .........................  pcs.                   ..............................  €             ..............................  €

Protection (optional position)

GEZE emergency stop switch with illuminated mushroom button for emergency opening or unlocking with two combined switch elements (C/O, O/O) for use with FR-RWS, enclosure rating IP 40

(  ) Surface-mounted   (  ) Flush-mounted



	1.18 
	             .........................  pcs.                  ..............................  €             ..............................  €
Monitoring (optional position)
GEZE end position sensor with Reed switch certified in accordance with VdS Class C, for installation in the sliding door drive for electronic monitoring of the door leaves (e.g. for external alarm system, building management system etc.).
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CAN interface for the connection to the building management

Technical data:
CAN interface galvanically isolated.
CAN extension module for automatic GEZE sliding door, revolving door and swing door drives as interface to connect to the GEZE building management system myGEZE Control.
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Building automation connection

Building automation and control system 
For the integration of escape door control units, swing door drives, sliding doors and automatic window systems into a building management system for the use of typical building automation and control functions.
An automation controller with the following profile must be used:
BACnet device of the type BACnet Building Controller (B-BC) with tested conformity to the BACnet standard ISO 16484-5

myGEZE Control System
...... Piece basic controller as a powerful embedded PC that supports the BACnet protocol. BACnet controller of type B-BC (BACnet Building Controller / protocol audit 14)
for the integration of GEZE field bus devices. The number of fieldbus devices is specified in the specifications.

The system must be able to provide the following components (incl. software licence):

· myGEZE Control basic controller, embedded PC incl. GEZE Library 
· Terminal system for connecting the GEZE CAN bus 
· Terminal system for the connection of GEZE window technology based on 
             the IQ box KNX  
· Terminal system for connecting digital binary input signals to
             Basis of potential-free contacts 
· Terminal system for connecting digital output signals based on
potential-free door closer or changeover contacts 24 V DC     
The number of terminal systems is to be determined by the supplier on the basis of the tendered products at field level.
In top hat rail housing, incl. power supply unit, required auxiliary terminals for internal potential distribution, bus supply and bus termination.
Standard housing dimensions:  W x H x D 300 x 400 x 200 mm 
Supply voltage: 230 V AC 
incl. the following services:
· Project planning and interface configuration of the offered networking system according to GEZE standard.

· Mechanical assembly, electrical connection, commissioning
              ...........  Option                   ..............................  €             ..............................  €
Optional additional services:

Creation of project-specific wiring schematics for product systems

The service includes: 
· Creation of one basic diagram per door type
· Creation of a wiring schematic for the installed door, window and safety technology product systems
· A change index is included; additional changes charged separately
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