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Panic lock set GEZE IQ lock AUT for double-leaf doors

Self-locking panic lock GEZE IQ lock AUT with motorised strike box and all necessary and tested components for double-leaf full panic doors in accordance with EN 179 and EN 1125.
The active leaf is also unlocked upon panic release of the passive leaf.

Panic unlocking via handle or panic bar.
Thank to motorised activation of the strike box, a fully automatic panic solution for two-leaf doors is possible.

Self-locking of both door leaves

Changeover function for unlocking from the outside and integrated electrical timeout function against maloperation in the active leaf.

Divided and separated cross latch for absolute load-free bolt projection without jamming even under preload.
Modes of operation active leaf: night-time, secure day, permanently unlocked
Secure day operation: electric strike function by means of targeted locking or release of the cross latch

Night-time operation: steel bolt with 20 mm bolt projection / motorised bolt entry less than 1 sec.

Permanently unlocked: bolt withdrawn and cross latch not locked
Modes of operation passive  leaf: night-time, permanently unlocked  

Night-time operation: rods are extend 20 mm to the top and the bottom of the door
Permanently unlocked: rods withdrawn
All necessary contacts are integrated in the lock/passive leaf and provide potential free feedback:

Bolt contact (with 95 % bolt projection)

Handle contact (with handle activation 10°)

Cylinder contact

Auxiliary latch contact (door open/door leaf enclosed)

Release contact (bolt completely in lock case and cross latch loose)

In case of fire alarm or power cut automatic changeover to mechanical basic and panic function as well as self-locking.

Prepared for installation of profile lock cylinders and with 9 mm square nut.

Closed and corrosion resistant steel lockcase in DIN dimensions,

lock face plate and strike box face plate made of stainless steel,

lock can be used for DIN left and right doors without conversion

Nominal voltage:                    12-24 V DC

Current consumption:             temporarily 250 mA at 24V; 500 mA at 12 V (incl. control unit)

Supplied in a set comprising:

- 1 pc  motor mortise lock IQ lock EL DL with face plate
- 1 pc  rod drive IQ AUT for motorised activation of the strike box with face plate
- 1 pc  mechanical strike box DL with face plate
- 1 pc  motor lock control unit MST 210

- 1 pc  connecting cable 12-core, 10 m

- 1 pc  cable duct open

- 1 pc  reed switch contact set

- 1 pc  strike plate for receiving the lock upwards

- 1 pc  switch lock

- 1 pc  tubular pipe for locking upwards 

- 1 pc  solid rod for locking downwards

- 1 pc  rod guide

- 1 pc  floor lock hollow

( ) IQ lock EL DL 9235 (centres 92 mm, backset 35 mm)

( ) IQ lock EL DL 9240 (centres 92 mm, backset 40 mm)

( ) IQ lock EL DL 9245 (centres 92 mm, backset 45 mm)

( ) IQ lock EL DL 7255 (centres 72 mm, backset 55 mm)

( ) IQ lock EL DL 7265 (centres 72 mm, backset 65 mm)

( ) IQ lock EL DL 7280 (centres 72 mm, backset 80 mm)
( ) IQ lock EL DL 7210 (centres 72 mm, backset 100 mm)
Accessories:

( ) 1 pc. power supply NT 19.2-24                            part no. 089862 (active leaf)
( ) 1 pc. power supply NT 1.5-24                                part no. 151425 (passive leaf)

( ) 1 pc. IO module IO 420
For use on fire protection doors IQ lock AUT must be operated with an emergency power backup and the GEZE IO module IO 420.

Besides, fittings in accordance with EN 179 or EN 1125 are necessary for use on escape and rescue routes or on fire protection doors:
For approved fittings, please refer to the currently valid certificate versions 0757-CPR-229-7013137-5-2 / 0757-CPR-229PANIK-7013137-4 to certify the durability. Only GEZE components tested and approved together in accordance with EN 179 and EN 1125 may be installed.
To ensure all functions of the IQ lock AUT a door closer system with closing sequence control and a carry bar are to be fitted. A suitable double-leaf swing door drive solution can also be used on the active leaf due to the motorised unlocking of the IQ lock AUT.

GEZE recommends

(  ) 1 pc Powerturn                                                                part no. 157088
or

(  ) 1 pc EMD F-IS                                                                 part no. 122037
or
(  ) 2 pc TS 5000                                                                   part no. 027333

(  ) 1 pc ISM guide rail                                                           part no. 115549
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