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	1.0 
	             .........................  pcs.                   ..............................  €             ..............................  €
GEZE ECdrive H
Automatic linear sliding door with low building depth, optimised for use in areas with increased hygiene requirements, TÜV type-tested in accordance with EN 16005, for leaf weights of up to 120 kg per leaf
Drive
Integrated rechargeable battery with automatic charge and monitoring functions for opening or closing in the event of a power failure
Ball bearing mounted rollers made of plastic for extremely smooth running and a long service life
Intelligent digital control unit (Category 2 in accordance with DIN EN 954-1 and Performance Level “d” in accordance with DIN EN ISO 13849-1):
- convenient parameter setting, commissioning and maintenance via optional Bluetooth connection to a PC 
- self-learning and with dynamic adaptation of the passage hold-open time for optimum convenience
- various Push & Go functions can be connected
- pre-configured switch functions optimised for use in medical areas (nurse opening, bed opening, cleaning opening)
- can be networked and integrated in building systems via CAN-bus
- independent error detection and logging
- adjustment options for all door movement parameters
- all functions integrated in one unit, no further modules necessary
Extremely quiet DC drive
Robust power supply with integrated all-pole main switch and fuse protection
Static and dynamic power limitation according to EN 16005, as well as static under 150 N in compliance with ASR A1.7 (formerly BGR 232)
Automatic reversal when an obstacle is detected
Construction dimensions (in unfinished state):
Clear overall height LH:............... mm
Clear construction width LB:............... mm
Passage height DH:.............. mm (2000 – 2400 mm)
Passage clearance DB:.......... mm (1-leaf 700 - 2200 mm, 2-leaf 900 - 2200 mm)
Door system version:
(  ) single-leaf closing on the left
(  ) single-leaf closing on the right
(  ) double-leaf
Leaf profile:
(  ) moving leaf with ISO or mono-glass fine-framed (up to 120 kg leaf weight)
(  ) with 22 mm ISO glass made of (  ) ESG or (  ) VSG
(  ) with 10 mm ISO glass made of (  ) ESG or (  ) VSG
(  ) with panel infill
Surface of the light alloy parts of the drive and the moving leaves if appropriate:
(  ) anodised EV1 or (  ) RAL ........
Wiring to be carried out on site according to the GEZE cable plan by an electrical contractor.
Installation, commissioning and instruction of the operator as well as documentation handover in compliance with EN 16005 through plant fitters or service partner.
In compliance with EN 16005:
- safety analysis must be carried out as a basis for planning and execution
- an inspection must be carried out at least once a year and maintenance at least once a year


	1.1 
	             .........................  pcs.                  ..............................  €             ..............................  €
Operation
GEZE display programme switch in the AS 500 range for setting the mode of operation as well as for commissioning the drive and setting parameters, with function keys, 2x 7-segment display, alphanumerical error display, IP40 rating
Modes of operation: permanently open, automatic, exit only, night-locking, off
(  ) surface mounting      (  ) flush mounting 
or
GEZE keypad programme switch for setting the mode of operation, with function keys, LED dot display, coded error display, IP40 rating, suitable for switch product ranges with 55 x 55 mm switch unit
Modes of operation: off, permanently open, automatic, exit only, night-locking
(  ) surface mounting      (  ) flush mounting 
or
GEZE mechanical programme switch for setting the mode of operation, LED error display, IP40 rating, suitable for switch product ranges with 55 x 55 mm switch insert
Modes of operation : off, permanently open, automatic, exit only, night-locking
(  ) surface mounting      (  ) flush mounting 
(  ) with rotary button      (  ) with key


	1.2 
	             .........................  pcs.                   ..............................  €             ..............................  €
Operation (optional position)
GEZE key switch to “lock” the programme switch to prevent unauthorised changing of the mode of operation, IP40 rating
(  ) surface mounting      (  ) flush mounting
(  ) Euro Profile half cylinder


	1.3 
	             .........................  pcs.                   ..............................  €             ..............................  €
Activation and protection (optional position)
GC 363+ combined detector with direction detecting radar movement detector for activation and active infrared detector with two light curtains for protection of the opening or closing area in accordance with EN 16005, IP54 rating, 10 possible light curtain configurations
Version:
( ) black
( ) according to RAL
(  ) outside   (  ) inside
Accessories:
(  ) outside: weather hood to protect the sensor from the interference of rain
(  ) Ceiling installation bracket
(  ) Ceiling installation kit for integrating the sensor in the ceiling



	1.4 
	             .........................  pcs.                   ..............................  €             ..............................  €
Activation and protection (optional position)
GC 365 combined detector with direction detecting radar movement detector for activation and active infrared detector with two light curtains for protection of the opening or closing area in accordance with EN 16005, IP54 rating, 4 possible light curtain configurations
Version:
( ) black
(  ) outside   (  ) inside
Accessories:
(  ) outside: weather hood to protect the sensor from the interference of rain
( ) Ceiling installation bracket
(  ) Ceiling installation kit for integrating the sensor in the ceiling


	1.5 
	             .........................  pcs.                   ..............................  €             ..............................  €
Protection (optional position)
GC 339+ active infrared detector with two light curtains for protecting the opening or closing area in accordance with EN 16005, IP54 rating, 10 possible light curtain configurations
Version:
( ) black
( ) according to RAL
( ) interior ( ) exterior
Accessories:
(  ) outside: weather hood to protect the sensor from the interference of rain
( ) Ceiling installation bracket
( ) Ceiling installation kit for integrating the active infrared detector in the ceiling


	1.6 
	Protection (optional position)
GC 341 active infrared detector with two light curtains for protecting the opening or closing area according to EN 16005, IP54 rating, 4 possible light curtain configurations
Version:
( ) black
( ) interior ( ) exterior
Accessories:
(  ) outside: weather hood to protect the sensor from the interference of rain
( ) Ceiling installation bracket
( ) Ceiling installation kit for integrating the active infrared detector in the ceiling



	1.7 
	             .........................  pcs.                  ..............................  €             ..............................  €
Activation (optional position)
GEZE elbow switch, plastic, IP30 rating
Dimensions: 90 x 180 x 23 mm 
(  ) white 
 (  ) stainless steel
( ) optional transmitting module 
(  ) surface mounting
(  ) Rear panel for attaching the elbow switch to glass (in connection with transmitting module)
or
GEZE elbow switch, LS990, IP30 rating
Dimensions: 81 x 223 x 51 mm
(  ) white  
(  ) stainless steel
( ) optional transmitting module 
(  ) surface mounting      (  ) flush mounting
or
GEZE elbow switch, stainless steel, IP65 rating
Dimensions: 72 x 250 x 17 mm 
(  ) surface mounting 
or
GEZE non-contact proximity switch (radar)

Plastic with antimicrobial surface, IP rating IP65, multi-colour LED feedback, adjustable acoustic feedback. Additional input to actively change the LED colour.

Dimensions: 80 x 80  mm

( ) Flush mounting 12 mm deep
( ) Surface mounting 21 mm deep
( ) Variant for WC
or
GEZE LED sensor push button, plastic, IP rating IP 69K
round, diameter: 100 mm
( ) Flush-mounted

( ) Surface-mounted: mounting ring flat 4 mm

( ) Surface-mounted: mounting ring high 20 mm
 
or
GEZE LED sensor push button, glass, IP rating IP 69K
round, diameter: 100 mm
( ) Flush-mounted

( ) Surface-mounted: mounting ring flat 4 mm

( ) Surface-mounted: mounting ring high 20 mm
or

GEZE LED sensor foot switch, glass, IP69K rating

Dimensions: 100 x 100 x 3 mm

(  ) flush mounting
(  ) vertically adjustable installation base for depths of up to 215 mm from the unfinished floor.


	1.8 
	             .........................  pcs.                   ..............................  €             ..............................  €
Activation (optional position)
GEZE wireless programme with secure rolling code encryption for wireless activation of the drive (approx. 30 m range in the building).
Transmitter:
(  )   remote control with 1 push button, IP54 rating and wall fixing
(  )   remote control with 2 push buttons, IP54 rating and wall fixing
(  )   remote control with 4 push buttons, IP54 rating and wall fixing
(  )   transmitting module for optional integration in GEZE elbow switches
Receiver:
(  )   receiving module with 2 outputs, 24 V, pulse mode only or pulse mode and continuous operation for mounting in the drive or in a flush-mounted socket with IP20 rating


	1.9 
	             .........................  pcs.                  ..............................  €             ..............................  €
Activation (optional position)

GEZE GCER 300, 1-door SET
Access control solution with RFID reader and PIN keypad in stand-alone operation for controlling one door (can be extended to 2 doors). RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Two authorisation types for short-time release or continuous release (office function). Configurable door release time. Variable PIN length. Communication between reader and control unit takes place by encrypted data transfer. Functions such as interlocking door system or dementia adjustable. Release buttons can be connected.
Set comprising:
1 pc. GEZE GCER 300 I/O Box (ID no. 185707)
1 pc. GEZE GCVR 300 T, RFID reader flush-mounted (ID no. 185708)
2 pc. GEZE GCER 300 system card master (ID no. 185713)
10 pc. GEZE RFID ID card (ID no. 185711)
Optional
GEZE GCVR Touch 300 T, RFID reader flush-mounted (ID no. 187108)
GEZE RFID key fob (ID no. 185712)
GEZE GCER AP surface-mounted frame (Id. no. 130024)

or

GEZE GCER 300 Light, 1-door SET
Access control solution with RFID reader and PIN keyboard in stand-alone operation with a relay output for controlling one door located in the secured inner area. RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised for short-time release. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Configurable door release time. Variable PIN length. Communication takes place via encrypted data transfer.
Set comprising:
1 pc. GEZE GCER 300 Light, RFID reader flush-mounted (ID no. 185710)
1 pc. GEZE GCER 300 system card master (ID no. 185713)
10 pc. GEZE RFID ID card (ID no. 185711)
Optional
GEZE RFID key fob (ID no. 185712)
GEZE GCER AP surface-mounted frame (ID no. 130024)

Accessories for GCER 300 / GCER 300 Light
Plug-in power supply NT 1.0 A – 24 V DC (optional)
Primary:  230 V AC, 50 Hz
Secondary: 24 V DC (+/- 5 %) / 1 A
(ID no. 130025)

Power supply NT 1.1 A – 24 V DC flush-mounted (optional)
For installation in deep standard flush-mounted boxes
Primary:  230 V AC, 50 Hz
Secondary: 24 V DC / 1.1 A
(ID no. 151426)
Power supply NT 1.5 A – 24 V DC HA (optional)
For installation on top hat rails 
Primary: 230 V AC, 50 Hz
Secondary: 21.6 – 26.4 V DC / 1.5 A
(ID no. 151425)

	1.10 
	             .........................  pcs.                   ..............................  €             ..............................  €
Activation (optional position)
GEZE key switch 
external (IP54 rating) with switch function, one-sided switching operation
(  ) with Euro profile half cylinder or (  ) without Euro profile half cylinder
(  ) surface mounting
      (  ) flush mounting


	1.11 
	             .........................  pcs.                  ..............................  €             ..............................  €
Activation (optional position)
GEZE key switch 
external (IP54 rating) with hold-open function for fire brigade, stay-put on two sides
(  ) with Euro profile half cylinder 
or (  ) without Euro profile half cylinder
(  ) surface mounting
      (  ) flush mounting


	1.12 
	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)
GEZE emergency stop switch with lighting for switching off the mains voltage, IP20 rating
An emergency control device (emergency stop switch) is not essential for compliance with EN 16005.
(  ) surface mounting      (  ) flush mounting


	1.13 
	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)
GEZE emergency stop switch with illuminated palm button for emergency opening or emergency unlocking, IP40 rating
An emergency control device (emergency stop switch) is not essential for compliance with EN 16005.
(  ) surface mounting      (  ) flush mounting


	1.14 
	             .........................  pcs.                  ..............................  €             ..............................  €
Locking (optional position)

(  ) two-stage electromagnetic locking integrated in the drive, with manual emergency unlocking
or
(  ) Lock M, manual hook bolt lock, prepared for Euro profile half cylinders for fine-framed moving leaves
(  ) with short cylinder 32 mm (16/16) on both sides, flush with profile, lockable on both sides 
(  ) with Euro profile half cylinder 40 mm (30/10), lockable on one side
(  ) with escutcheon plate  for the installation of Euro profile half cylinder, e.g. 
(  ) Euro profile double cylinder on-site for integration in an on-site closing system.
Note: Euro profile cylinders which project beyond the profile represent danger zones. The opening width must be restricted here.
or
( ) Lock A, automatic hook bolt lock with manual emergency unlocking, for fine-framed moving leaves, quick and reliable locking and unlocking of the door in night-time operation, locking profile invisibly integrated in the profile.
(  ) with 1 locking point
(  ) with 2 locking points
or
(  ) bolt lock for installation on the underside of the moving leaf (only for fine-framed moving leaves), prepared for Euro profile cylinder or Euro profile half cylinder
(  ) lockable on one side (for 46 mm Euro profile half cylinder) or 
(  ) lockable on both sides (for 71 mm Euro profile cylinder)


	1.15 
	             .........................  pcs.                  ..............................  €             ..............................  €
Floor guide (optional position)
Continuous floor guide made of aluminium, anodised  E6 C-0 (EV1), can be installed flush in the floor, guide rail can be removed for cleaning or replaced
Recommended for external doors with opening widths greater than 2000 mm
(  ) with floor guide drainage


	1.16 
	             .........................  pcs.                   ..............................  €             ..............................  €
Monitoring (optional position)
GEZE end position sensor with Reed switch certified in accordance with VdS Class C, for installation in the sliding door drive for electronic monitoring of the door leaves (e.g. for external alarm systems, building management system etc.).


	1.17 
	             .........................  pcs.                  ..............................  €             ..............................  €
CAN interface for the connection to the building management

Technical data:
CAN interface galvanically isolated.
CAN extension module for automatic GEZE sliding door, revolving door and swing door drives as interface to connect to the GEZE building management system myGEZE Control.
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