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	1.0 
	             .........................  pcs.                  ..............................  €             ..............................  €

GEZE ECturn Inside
1-leaf, can be integrated directly into on-site single-action doors (minimum door thickness 55 mm), as a low-noise electromechanical swing door drive for internal doors.

Tested and certified in accordance with 16005.

Intelligent digital control (category 2 in accordance with DIN EN 954-1 and Performance Level D in accordance with DIN EN ISO 13849-1).

Version:

(  ) integrated in the door leaf

(  ) integrated in the frame

Functions:

Operation modes: permanently open, automatic, night

Low-energy mode (low-energy drive) in accordance with EN 16005,

automatic mode,

obstruction detection and reversing,

diagnosis function and fault memory,

all settings can be made directly on the drive or via the display programme switch

Technical features:

Mains connection: 230/110 V AC, 50/60 Hz,

door width: max. 1100 mm,

door weight: max. 125 kg,

door opening angle: approx. 110°,

opening and closing speed adjustable,

hold-open time adjustable from 0 to 30 seconds

Contour-controlled opening and closing

Connection possibilities:

Separate inputs for inner and outer sensors,

optional rechargeable battery to be able to guarantee automatic opening and 
closing even in the event of a power failure

Emergency-stop switch, programme switch, motor lock,

power supply for external devices: 24 V DC, 600 mA

Wiring to be carried out on site by an electrical contractor according to the GEZE cable diagram, start-up to be carried out by plant fitters or service partner.

In accordance with EN 16005:

- Safety analysis must be carried out as a basis for planning and execution

- Maintenance and accident prevention inspection must be carried out at least once per year

- The secondary closing edge of an automatic single-action door must be protected

If there is no protection, the safety analysis must refer to the residual risk.

Protection of the secondary closing edge is to be carried 
out on site and is not part of the scope of delivery of GEZE GmbH.

We therefore recommend the use of a finger protection 
screen or round profiles to protect the secondary closing edge.

Guide rail / lever in the colour:

(  ) anodised EV 1
(  ) RAL .....


	1.1 
	             .........................  pcs.                  ..............................  €             ..............................  €

A5000—E (optional position)
Compact electric strike 
in working current version, 

with signal processor and low-current mode,
approved for use on smoke protection doors,

for universal use DIN right / left

with 3 mm adjustable radius latch,

Latch engagement depth: 6 mm

with bipolar EMC protective diode,

Retention force: 5000 N

Nominal voltage for permanent operation: 8 - 24 V AC/DC

Current consumption: 200 mA (at 8 – 11 V)

Current consumption: 50 mA (at 12 – 24 V)

Dimensions: 
15.8 x 59.5 x 25.5 mm (W x H x D)

Without strike plate



	1.2 
	             .........................  pcs.                  ..............................  €             ..............................  €

Protection (optional position)

GEZE rechargeable battery for maintaining the function of the swing door drive ECturn even in the event of a power failure



	1.3 
	             .........................  pcs.                  ..............................  €             ..............................  €
Protection (optional position)

GEZE GC 342 laser scanner, tested in accordance with EN 16005, mounted on the door leaf, to protect the swivelling range of interior and exterior doors in the opening and closing direction. Robust enough to handle all floor conditions (e.g. entrance mat, metal rail, dark and absorbing flooring, shiny and wet tiles, grating). With integrated wall blanking and dynamic main closing edge protection.
Door leaf width: ....... mm
( ) GC 342 laser scanner kit (contains two sensors to protect both sides of the leaf)
IP rating IP54, with optimised secondary closing edge protection. If fingers are very likely to be trapped, an additional mechanical solution on the secondary closing edge can be considered. The secondary closing edge protection near the door hinges must be carried out on-site or by the door manufacturer on the basis of the safety analysis.
( ) GC 342 for hinge side and GC 342+ for the opposite hinge side
Combination of GC 342, IP rating IP54 for the hinge side and GC 342+, IP rating IP44 for the opposite hinge side. Each as an individual module (left and right variants)
 
Version:
( ) stainless steel colour
( ) black
( ) white
 
( ) Fire protection kit - master-slave replacement cable which enables cables to be guided through 5 mm instead of 10 mm bore-holes. The drilling permit must be requested from the door manufacturer.
Retrofit circuit board for connection to door cables fitted on site
( ) GC 342 Retrofit-Interface

( ) GC 342+ Retrofit-Interface

Only available for GC 342:
Protective cover to protect the laser scanner against interferences
( ) stainless steel colour
( ) black
( ) according to RAL
 


	1.4 
	             .........................  pcs.                  ..............................  €             ..............................  €

Protection (optional position)
GEZE safety sensors kit, in sleek narrow strip with IP rating 52, type-approved in accordance with EN 16005, installed on the door leaf, for protecting the door's swivelling range in the opening and closing direction. With integrated wall blanking (kit contains 2 safety sensors for protecting both leaf sides)
Door leaf width: ....... mm
(  ) GC 338 safety sensor kit for internal and external doors and all floor conditions (e.g. floor mat, metal rail, dark and absorbing flooring, shiny and wet tiles, grating).

Version:
( ) EV1
( ) according to RAL
(  ) GC 338 rain cover to protect the safety sensor against interference caused by rain

The secondary closing edge protection near the door hinges must be carried out on site or by the door manufacturer on the basis of the safety analysis.


	1.5 
	             .........................  pcs.                  ..............................  €             ..............................  €

Protection (optional position)

GEZE emergency stop switch with glass pane and light for switching off the mains voltage, enclosure rating IP 20

(  ) Surface-mounted (  ) Flush-mounted

An emergency command device (emergency stop switch) is not essential in accordance with EN 16005.



	1.6 
	             .........................  pcs.                  ..............................  €             ..............................  €

Activation (optional position)

GC 308 radar movement detector with direction detection and cross-traffic fade-out for activation, IP 54 rating, multi-colour LED feedback

Dimensions (WxHxD): 120 x 50 x 50 mm

Version:

(  ) black 

(  ) white 

(  ) stainless steel colour 

(  ) outside   (  ) inside

Accessories:

(  ) Ceiling installation kit

(  ) Ceiling bracket

(  ) exterior: weather hood


	1.7 
	             .........................  pcs.                  ..............................  €             ..............................  €

Activation (optional position)

GC 302 radar movement detector with direction detection and cross-traffic fade-out for activation, IP rating IP 54

Dimensions (WxHxD): 176 x 62 x 52 mm

Version:

(  ) black 

(  ) acc. to RAL

(  ) outside   (  ) inside

Accessories:

(  ) Ceiling installation kit

(  ) exterior: weather hood



	1.8 
	             .........................  pcs.                  ..............................  €             ..............................  €

Activation (optional position)

GEZE elbow switch, plastic, IP rating IP 30
Dimensions: 90 x 180 x 23 mm 
( ) white  ( ) stainless steel
( ) optional transmitting module 
( ) Surface-mounted  ( ) Rear panel for attaching the elbow switch to glass (in connection with the transmitting module)
or
GEZE elbow switch, LS990, IP rating IP 30
Dimensions: 81 x 223 x 51 mm
( ) white  ( ) stainless steel
( ) optional transmitting module 
( ) Surface-mounted ( ) Flush-mounted
or
GEZE elbow switch, stainless steel, IP rating IP 65
Dimensions: 72 x 250 x 17 mm 
( ) Surface-mounted
 
or
GEZE non-contact proximity switch (radar)
Plastic with antimicrobial surface, IP rating IP65, multi-colour LED feedback, adjustable acoustic feedback. Additional input to actively change the LED colour.

Dimensions: 80 x 80  mm

( ) Flush mounting 12 mm deep
( ) Surface mounting 21 mm deep
 
or
GEZE LED sensor push button, plastic, IP rating IP 69K
round, diameter: 100 mm
( ) Flush-mounted

( ) Surface-mounted: mounting ring flat 4 mm

( ) Surface-mounted: mounting ring high 20 mm
 
or
GEZE LED sensor push button, glass, IP rating IP 69K
round, diameter: 100 mm
( ) Flush-mounted

( ) Surface-mounted: mounting ring flat 4 mm

( ) Surface-mounted: mounting ring high 20 mm
or
GEZE LED sensor foot switch, glass, IP rating IP69K

Dimensions: 100 x 100 x 3 mm

( ) flush-mounting

( ) vertically adjustable installation base for depths of up to 215 mm from the unfinished floor



	1.9 
	             .........................  pcs.                  ..............................  €             ..............................  €

Activation (optional position)

GEZE wireless programme with secure rolling code encryption for wireless drive activation (range of approx. 30 m in the building).

Transmitter:

(  )   Wireless transmitter with 1 key, enclosure rating IP 54 and wall fixing

(  )   Wireless transmitter with 2 keys, enclosure rating IP 54 and wall fixing

(  )   Wireless transmitter with 4 keys, enclosure rating IP 54 and wall fixing

(  )   Wireless transmitter module for optional integration in the GEZE elbow switch

Radio receiver:

(  )   Radio receiver module with 2 outputs, 5 V, pulse mode or pulse and
        permanent mode for mounting in the drive 



	1.10 
	             .........................  pcs.                  ..............................  €             ..............................  €

Activation (optional position)

GEZE GCER 300, 1-door SET
Access control solution with RFID reader and PIN keypad in stand-alone operation for controlling one door (can be extended to 2 doors). RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Two authorisation types for short-time release or continuous release (office function). Configurable door release time. Variable PIN length. Communication between reader and control unit takes place by encrypted data transfer. Functions such as interlocking door system or dementia adjustable. Release buttons can be connected.
Set comprising:
1 pc. GEZE GCER 300 I/O Box (ID no. 185707)
1 pc. GEZE GCVR 300 T, RFID reader flush-mounted (ID no. 185708)
2 pc. GEZE GCER 300 system card master (ID no. 185713)
10 pc. GEZE RFID ID card (ID no. 185711)
Optional
GEZE GCVR Touch 300 T, RFID reader flush-mounted (ID no. 187108)
GEZE RFID key fob (ID no. 185712)
GEZE GCER AP surface-mounted frame (Id. no. 130024)

or

GEZE GCER 300 Light, 1-door SET

Access control solution with RFID reader and PIN keyboard in stand-alone operation with a relay output for controlling one door located in the secured inner area. RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised for short-time release. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Configurable door release time. Variable PIN length. Communication takes place via encrypted data transfer.
Set comprising:
1 pc. GEZE GCER 300 Light, RFID reader flush-mounted (ID no. 185710)
1 pc. GEZE GCER 300 system card master (ID no. 185713)
10 pc. GEZE RFID ID card (ID no. 185711)
Optional
GEZE RFID key fob (ID no. 185712)
GEZE GCER AP surface-mounted frame (ID no. 130024)

Accessories for GCER 300 / GCER 300 Light
Plug-in power supply NT 1.0 A – 24 V DC (optional)
Primary:  230 V AC, 50 Hz
Secondary: 24 V DC (+/- 5 %) / 1 A
(ID no. 130025)

Power supply NT 1.1 A – 24 V DC flush-mounted (optional)
For installation in deep standard flush-mounted boxes
Primary:  230 V AC, 50 Hz
Secondary: 24 V DC / 1.1 A
(ID no. 151426)
Power supply NT 1.5 A – 24 V DC HA (optional)
For installation on top hat rails 
Primary: 230 V AC, 50 Hz
Secondary: 21.6 – 26.4 V DC / 1.5 A
(ID no. 151425)
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	             .........................  pcs.                  ..............................  €             ..............................  €

Opening restrictor (optional position, an opening restrictor is necessary)

GEZE door stop to protect the door and its direct environment.



	1.12 
	             .........................  pcs.                  ..............................  €             ..............................  €

Opening restrictor (optional position, an opening restrictor is necessary)

GEZE integrated opening restrictor, can also be retrofitted to the guide rail on site.

Area of application: internal doors



	1.13 
	             .........................  pcs.                  ..............................  €             ..............................  €

Operation (optional position)

GEZE display programme switch in the AS 500 range for setting the mode of operation as well as for putting the drive into operation and setting parameters, with function keys, 2x 7-segment display, alphanumerical fault display, IP rating IP 40
Operating modes: permanently open, automatic, shop closing, night-locking
( ) Surface-mounted ( ) Flush-mounted


	1.14 
	             .........................  pcs.                  ..............................  €             ..............................  €

Operation (optional position)

GEZE key switch to “lock” the programme switch to prevent unauthorised changing of the operating mode, enclosure rating IP 40

(  ) Surface-mounted (  ) Flush-mounted
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